Hurricane Valley, Inc.

# Professional Engineering Consultants

## P.O. Box 118 (72089)    1506 Pricket Road

Bryant, AR

### Tel  501-847-7282

#### STORM WATER DETENTION CALCULATIONS

Arkansas Storage Centers, IX, LLC

2615 Shady Pine

Bryant, Arkansas

August 1, 2021

(Revised March 3, 2022)

PROJECT DESCRIPTION

This project consists of a open storage area for RVs on an approximately 6.96 acre site. Approximately 4.18 acres will be disturbed. Area 1 containing 2.1 acres and Area 2 containing 1.86 acres will each have a  detention pond.

DETENTION PLAN

The construction activity shall consist of grading approximately 3.96 acres of surface area by shaping the area with cuts and fills. Area 1 and area 2 will each contain a detention pond as shown on the Detention Plan.

Open storage units shall be constructed with gravel or crushed stone in-lieu of paving.

During grading hay bales and/or silt screen will be placed around the construction area as required.

DETENTION POND CALCULATIONS

The present runoff coefficient for the existing undisturbed area is about 0.44. The runoff coefficient of the site after construction is completed is expected to be 0.92 for the paved areas and the roof areas and 0.50 for graveled or crushed rock areas..

Total Area = 3.96 acres

Area 1   (2.42 acres)

Pre-development

Flow Dist.   L = 300 LF @ 3% slope

Conc. Time (Tc)  =  17 min.

Return Period  =   10 years       Intensity =   5.0 in/hr

Return Period  =   25 years       Intensity =   5.8 in/hr

Coefficient (undev)  =  0.44

Road  0.19 ac

Not detained    0.06 ac

Q (undev) = Aci = (2.60- 0.23- 0.06) x 0.44 x 5.8 = 5.90 cfs

Q (undev) = Aci = (0.23) x 0.92 x 5.8 =                    1.23 cfs

Total   7.13 cfs

Discharge Design  (max. low flow)

Return Period  =   10 years       Intensity =   5.0 in/hr

Q (undev) = Aci = (2.31) x 0.44 x 5.0 =  5.08 cfs

Post Development

Conc. Time (Tc)  =  5 min.

Return Period  =   25 years       Intensity =   8.5 in/hr

Coefficient (undev)  =  0.44

Roof Tops = 0.85 ac

Gravel  1.79 ac

Not detained    0.06 ac

Q (undev) = Aci = 1.27 x 0.5 x 8.5 =   7.61 cfs

Q (undev) = Aci = 0.81 x 0.92 x 8.5 = 6.33 cfs

Total   13.94 cfs

##### Approximate Area which can not be detained is 0.06 acres.

Q (dev) = Aci = 0.06 x 0.44 x 5.8 =  0.15 cfs

##### Detention Pond Volume Required    (Will use underground detention)

Diff. = 13.94 – 7.13  +  0.15 = 6.96 cfs

V = 6.96 x Tc x 60 = 6.96 x 5 x 60 = 2088   Use 2100 CF

280 ft. of 36”dia. HDPE pipe at 7.07SF per foot  =  1980 CF

60 ft. of 18” dia. HDPE pipe at 1.75 SF per foot  =    105 CF

Junction and Inlet boxes                                        =    50 CF

`			Total Storage Volume                   2118 CF > 2100 CF

Low Flow Pipe in Junction Box Weir

10 inch PVC pipe

Q = CA (2gh)1/2  = 0.6(0..545)((2)(32.2)(3))1/2 = 4.5 cfs  <  5.08 cfs

##### Overflow Weir  in Junction Box

##### Return Period 100 years  Intensity = 10 in/hr

Q (undev) = Aci = 1.27 x 0.5 x 10 =   6.35 cfs

Q (undev) = Aci = 0.70 x 0.92 x 10 = 6.44 cfs

Total   12.79 cfs

12.79 – 4.62 = 8.17

4 LF with 9” deep flow = 8.32 cfs > 8.17 cfs cfs

Area 2   (1.86 acres)

Pre-development

Flow Dist.   L = 400 LF @ 4% slope

Conc. Time (Tc)  =  17 min.

Return Period  =   10 years       Intensity =   5.0 in/hr

Return Period  =   25 years       Intensity =   5.8 in/hr

Coefficient (undev)  =  0.44

Not detained  = 0.27 ac

Q (undev) = Aci = (1.86 - 0.27) x 0.44 x 5.8 = 4.06 cfs

Discharge Design (max. low flow)

Q (undev) = Aci = (1.86) x 0.44 x 5.0 =  4.09 cfs

Post Development     Area 2 (1.86 acres)

Conc. Time (Tc)  =  5 min.

Return Period  =   25 years       Intensity =   8.5 in/hr

Coefficient (undev)  =  0.44

Roof Tops = 0.56 ac

Gravel  1.86 – 0.27 – 0.56 = 1.03 ac

Not detained   =  0.27 ac

Q (undev) = Aci = 1.03x 0.5 x 8.5 =   4.38 cfs

Q (undev) = Aci = 0.56 x 0.92 x 8.5 = 4.38 cfs

Total     8.76 cfs

##### Approximate Area which can not be detained is 0.27 acres.

Q (dev) = Aci = 0.27 x 0.44 x 5.8 =  0.69 cfs

##### Detention Pond Volumn Required

Diff. = 8.76 – 4.06  +  0.69 = 5.39 cfs

V = 5.39 x Tc x 60 = 5.28 x 5 x 60 = 1617 CF      Use 1700 CF

Detention Pond 2 (2000 CF)  Discharge

Allowable low flow discharge  4.09 cfs

10 inch PVC pipe

Q = CA (2gh)1/2  = 0.6(0.545)((2)(32.2)(1.5))1/2 = 3.21 cfs  < 4.09 cfs

##### Detention Pond 2 Spillway

##### Return Period 100 years  Intensity = 10 in/hr

Q (undev) = Aci = 1.06 x 0.5 x 10 =   5.30 cfs

Q (undev) = Aci = 0.53 x 0.92 x 10 = 4.88 cfs

Total     10.10 cfs

10.10 – 3.21 = 6.89 cfs

5 LF with 8” deep flow = 8.81 cfs > 6.89 cfs cfs

CONTRACTOR

The contractor has not been determined.

Respectfully submitted,

Charles F. Best, P.E.